## Cover Sheet
BILL OF QUANTITIES
NEW NATIONAL HOSPITAL
MARGETSON HOUSE REFURBISHMENT
St. John, Montserrat
4 APRIL 2023
Prepared By
Rider Levett Bucknall (St. Lucia) Ltd.
Mercury Court
Choc Estate
P.O. Box CP5747
Castries, St. Lucia
T: 1 758 452 2125 / 6
RLB.com

## Contents
NEW NATIONAL HOSPITAL
MARGETSON HOUSE REFURBISHMENT
ST. JOHN,
MONTSERRAT
CONTRACTOR'S NAME:
| CONTRACT AMOUNT: |  | 0
CONDITIONS OF CONTRACT
BILLS OF QUANTITIES
APRIL 2023
CONTENTS
Bills of Quantities
| 1 | Preliminaries and General Conditions
| 2 | Schedule of Drawings
| 3 | Measured Works
| 4 | Summary

## GD
NEW NATIONAL HOSPITAL ST. JOHN, MONSTERRAT
MARGETSON HOUSE REFURBISHMENT
GENERAL CONDITIONS

## General
NEW NATIONAL HOSPITAL
BILL OF QUANTITIES
MARGETSON HOUSE REFURBISHMENT
GENERAL CONDITIONS
NAMES OF PARTIES
a | "Employer" Shall mean -
| Ministry of Health | Telephone:
| E.K. Osbourne Building | Fax:
| Little Bay | Email:
Montserrat
b | "Architect" shall mean -
| Article 25 Humanitarian Architecture | Telephone: +44 (0)20 3197 9800
| 1 Canada Square | Email: joseph-davis@article-25.org
| E14 5AB | Web: www.article-25.org
United Kingdom
c | "Structural Engineer" shall mean -
| Clarkebond | Telephone: +44 (0) 1392 369098
| GF Suite, Bickleigh House | Fax: +44 (0) 1392 369100
| Park Five Business Centre, | Email: exeter@clarkebond.co.uk
| Sowton, Exeter EX2 7HU | Web: www.clarkebond.com
d | "Quantity Surveyor" shall mean -
| Rider Levett Bucknall (St. Lucia) Ltd | Telephone: (758) 452 2125
| Mercury Court, Choc Estate | Email: david.piper@lc.rlb.com
| P.O. Box CP5745, | Web: www.rlb.com
Castries, St. Lucia
e | DESCRIPTION OF WORKS
The works comprise the refurbishment of an existing two level concrete building.
This includes demolition, partitioning, changes to floor, wall and ceiling finishes, electrical, plumbing, HVAC. Adding stair cases, widening main entrance etc.
There are offices, labortories, washrooms, kitchen, storage, service closets etc.
GENERAL MATTERS
e | ACCESS TO SITE
Access will be through the main entrance to the hospital site as agreed with the GoM Supervisor and Hospital Director
f | METHOD OF MEASUREMENT
The Bills of Quantities have been prepared generally in accordance with the Principles of Measurement (International) For Works of Construction 1st Edition June 1979 issued by the Royal Institution of Chartered Surveyors.
g | LEVELS AND SETTING OUT THE WORKS
The Architect shall determine any levels which may be required for the execution of the Works, and shall furnish to the Contractor by way of accurately dimensioned drawings such information as shall enable the Contractor to set out the Works at ground level. Unless the Architect shall otherwise instruct, in which case the contract sum shall be adjusted accordingly, the Contractor shall be responsible for and shall entirely at his own cost amend any errors arising from his own inaccurate setting out.
h | FOREMAN-IN-CHARGE
The Contractor shall constantly keep upon the Works a competent foreman-in-charge and any instructions given to him by the Architect shall be deemed to have been issued to the Contractor.
i | CURRENCY
All reference to currency in this Contract is to Eastern Caribbean Currency.
j | LABOUR LEGISLATION
The Contractor shall comply with all labour legislation in accordance with the requirements of the Government of Montserrat.
The Contractor shall be solely responsible for obtaining and paying for necessary work permits if required for his personnel.
The Contractor shall abide by the decision of the Government in respect of the employment of non Montserratians.
k | TENDER AND CONTRACT DOCUMENTS
The Contractor shall not make any alterations to the tender or contract document except on the written instructions of the Quantity Surveyor.
If any unauthorized amendment is made it shall be ignored and the original text adhered to.
The Contractor is advised to rate and extend every item in the Bill of Quantities for which he requires payment. Any item left unpriced shall be deemed to be allowed for in his rates of other items or elsewhere in the tender. No claim in respect of unpriced items shall be entertained.
l | HANDOVER OF COMPLETED WORK
A provisional date for handing over the work shall be agreed and approximately two weeks prior to this the Architect, subject to his being satisfied that the work is in such a state of readiness shall compile a 'snag' list of omitted and/or defective items and the formal handover shall not take place until all items on the 'snag' list have been completed or remedied.
The Architect shall arrange for the formal handover normally within one week after satisfactory completion by the Contractor of the 'snag ' list.
At the formal handover, a responsible representative of the Contractor shall accompany the Architect together with such other representatives that the Architect may deem necessary, on an inspection of the Works and if such an inspection shows the Works to be completed in every respect the Works shall be taken over. Any minor omissions and/or defects found to exist at this point shall be remedied by the Contractor within seven days.
m | DUTIES AND TAXES
Goods and materials imported for use on this project will be subject to import duty or to VAT at the port of entry. Items purchased locally will be subject to VAT where applicable.
The Contractor should allow for complying with the requirements of the various government departments for preparation and approval of Customs Entries etc.
n | PLANT, TOOLS AND VEHICLES
Allow for providing, maintaining and removing on completion all plant, vehicles, consumable stores and equipment necessary for the proper execution of the Works.
o | SAFETY, HEALTH AND WELFARE
Allow for provision of welfare and safety measures to the standard laid down in the local Welfare Regulations during the Contract, including measures in respect of those employed on the site by Nominated Sub-Contractors.
Allow also for providing an adequate First Aid Kit on site, and for providing industrial safety helmets to all authorized visitors on the site.
p | PAYMENT UNDER STATUTES
Allow for all costs in connection with National Insurance and Pensions.
Allow for all costs in connection with Workmen's Compensation Insurance.
Allow for all costs in connection with any other statute.
Allow for all costs in connection with payments under National Labour Agreements.
Allow for all costs incurred in respect of Annual and Public Holidays.
Allow for costs in respect of transporting people to and from the site.
q | PAYMENT UNDER STATUTES CONT'D
Allow for all other costs and expenses incurred under the National and Local Rules of the Building and Civil Engineering Industries Agreements.
r | WATCHING AND LIGHTING
Allow for watching and lighting and other protection necessary for the security of the Works, materials and plant also for the security of the public.
s | WORK TO OR AFFECTING ADJOINING PROPERTY
The Contractor shall give the Architect seven clear days notice in writing before executing work to or affecting adjoining properties.
t | MAINTENANCE OF ROADS ETC.
The Contractor shall be held responsible for any damage caused by him, his workpeople, Sub-Contractors or Suppliers to verges, trees, shrubs, fences, boundary walls, gates, drains and services during the currency of the contract or his attendance during the defects liability period and shall make good at his own expense to the satisfaction of the Local and/or other authorities and/ or owner.
The Contractor shall keep all roads, paths etc. free from dirt or debris and any obstruction associated with the works which would prejudice the safe and normal use of the said roads and paths.
u | POLICE REGULATIONS
Allow for complying with police regulations and local bye-laws.
v | TRESPASS AND NUISANCE
Allow for taking all necessary precautions to avoid inconveniencing adjoining owners or occupiers.
No workpeople employed on the Works shall be allowed to trespass upon adjoining properties. If the execution of the Works require workpeople to enter adjoining property, the necessary permission shall first be obtained by the Contractor who shall see that these instructions are carried out. The Contractor shall indemnify the Employer against any claim or action arising out of any trespass or other misconduct of the Contractor's, Sub-Contractor's and Suppliers' employees. The Contractor shall not obstruct any public way or do anything that shall amount to a nuisance or annoyance and shall in no way interfere with any right of way or right to adjoining property and any notice served on him or left at site requiring the discontinuance or suspension of the works shall be immediately forwarded by him to the Architect, or in the event of it being given verbally, shall immediately be communicated by him to the Architect and he shall keep the Employer indemnified against any claim or loss arising out of any act, neglect or omission of the Contractor, his Sub- Contractor or Suppliers in this respect.
w | SITE SUPERVISION
Allow for site supervision, including transportation, overheads and other associated costs.
x | TEMPORARY WATER
Allow for all necessary water for the Works from an approved source including removal upon completion
y | TEMPORARY LIGHTING AND POWER
Allow for all necessary electrical and lighting for the Works from an approved source including removal upon completion
z | TEMPORARY BUILDINGS AND RATES
Provide, maintain and remove on completion temporary offices, messrooms, sheds, sanitary accommodation (including for use of the Sub-Contractors) and other temporary buildings for use of the Contractor all in accordance with the statutory regulations; colour of external paintwork to be approved by the Architect.
aa | TEMPORARY HOARDINGS
Provide, maintain and remove on completion temporary fencing, hoardings, fans, planked footway, guard rails, gantries and the like for the proper execution of the work, for the protection of the public and for meeting the requirements of any local or other authority.
bb | TEMPORARY ROADS
Provide and maintain all necessary temporary roads, hard-standings and crossings on site.
cc | ADVERTISEMENTS
No advertisements shall be displayed except those specifically approved in writing by the Architect.
dd | SCAFFOLDING
Provide, maintain and remove on completion all necessary temporary scaffolding and staging.
ee | SAMPLES
Allow for submitting customary samples of materials and goods to the Architect and obtaining his approval.
ff | TESTING
Allow a Provisional Sum for the testing of materials and workmanship.
gg | PROTECTION
Allow for protection of all works including temporary casings, coverings, planked barrow runs, padding for ladders and scaffolding bearing on the work and all other measures to protect the work from damage or soiling.
The Contractor shall not permit anything to be done that is calculated to injure the stability of the Works or building and no cutting through walls or floors shall be done other than as indicated by the drawings or as described herein without the sanction of the Architect and the Contractor shall be held responsible for all damage arising through carelessness or inadvertence in this respect.
hh | PROTECTION FROM WEATHER
Allow for covering up and protecting the works from inclement weather.
ii | REMOVING RUBBISH AND CLEANING
Allow for clearing up and removing rubbish as it accumulates during the progress of the works and on completion clear up and remove all surplus materials, clean all glass, clean all sanitary fittings, remove all spots, splashes and stains, clean up all surfaces and leave the Works and site clean, sound and in perfect order to the satisfaction of the Architect.
jj | ATTENDANCE TO NOMINATED SUB CONTRACTORS
Allow for MEP or any other subcontractor.
SCHEDULE OF DRAWINGS & SPECIFICATIONS USED
ARCHITECTURAL DRAWINGS
DR-1000 | Site Plan |  | 10 Mar 2023
DR-1010 | Location Plan |  | 10 Mar 2023
DR-0100 | Ground Floor Demolition Plan |  | 10 Mar 2023
DR-0190 | Lower Ground Floor Demolition Plan |  | 10 Mar 2023
DR-1100 | Ground Floor Plan |  | 10 Mar 2023
DR-1190 | Lower Ground Floor Plan |  | 10 Mar 2023
DR-1300 | Ground Floor Finishes Plan |  | 10 Mar 2023
DR-1390 | Lower Ground Floor Finishes Plan |  | 10 Mar 2023
DR-1500 | Ground Floor Equipment Plan |  | 10 Mar 2023
DR-1590 | Lower Ground Floor Equipment Plan |  | 10 Mar 2023
DR-1600 | Ground Floor Fire Stategy |  | 10 Mar 2023
DR-1690 | Lower Ground Floor Fire Stategy |  | 10 Mar 2023
DR-3102 | West Elevation |  | 10 Mar 2023
DR-4100 | Cross Building Section |  | 10 Mar 2023
DR-4101 | Entrance Bridge Section |  | 10 Mar 2023
DR-8100 | Kitchen Extension Details |  | 10 Mar 2023
DR-8200 | Wall Type Details |  | 10 Mar 2023
DR-8300 | Door and Window Details |  | 10 Mar 2023
SH-8600 | Finishes and Equipment Schedule |  | 10 Mar 2023
SH-8650 | Door Schedule |  | 10 Mar 2023
SP-8900 | Architectural Specifications |  | 10 Mar 2023
STRUCTURAL DRAWINGS
10 | Lower Ground Floor Existing |  | 2023-03-01
11 | Ground Floor Existing |  | 2023-03-02
12 | First Floor Existing |  | 2023-03-03
13 | Existing sections |  | 2023-03-04
14 | 3D Views Existing |  | 2023-03-05
20 | Lower Ground Floor Proposed |  | 2023-03-06
21 | Ground Floor Proposed |  | 2023-03-07
22 | Proposed Works Area 2 |  | 2023-03-08
23 | Proposed Works Area 3 |  | 2023-03-09
24 | Proposed Works Area 4 |  | 2023-03-10
26 | Proposed Works Area 6 |  | 2023-03-11
27 | Proposed Works Area 7 Demolition |  | 2023-03-12
28 | Proposed Works Area 7 |  | 2023-03-13
29 | Proposed Drainage Plan |  | 2023-03-14
MEP DRAWINGS
E-700-001 | Lower Ground Floor Proposed Small Power |  | 2023-03-01
E-700-002 | Ground Floor Proposed Small Power |  | 2023-03-01
E-708-001 | Lower Ground Floor Proposed Lighting & Emergency Lighting |  | 2023-03-01
E-708-002 | Ground Floor Proposed Lighting & Emergency Lighting |  | 2023-03-01
E-755-001 | Lower Ground Floor Proposed Fire Alarms |  | 2023-03-01
E-755-002 | Ground Floor Proposed Fire Alarms |  | 2023-03-01
E-700001-DB | Distribution Board Schedule |  | 2023-03-01
M-604-001 | Lower Ground Floor Space Cooling |  | 2023-03-01
M-604-002 | Ground Floor Space Cooling |  | 2023-03-01
M-654-001 | Lower Ground Floor Ventilation |  | 2023-03-01
M-654-002 | Ground Floor Ventilation |  | 2023-03-01
M-604001 | Split Heat Pumps Schedule |  | 2023-03-01
M-654001 | Fan Schedule |  | 2023-03-01
M-654002 | Air Terminals Schedule |  | 2023-03-01
M-654003 | Louvres Schedule |  | 2023-03-01

## MHBOQ
NEW NATIONAL HOSPITAL ST. JOHN, MONSTERRAT
MARGETSON HOUSE REFURBISHMENT
BILL OF QUANTITIES

## Measured Works
NEW NATIONAL HOSPITAL
MARGETSON HOUSE REFURBISHMENT
BILL OF QUANTITIES
Ref | Description | Unit | Qty | Rate EC$ | Total Cost EC$
02 EXISTING CONDITIONS
D2010 | Plumbing Fixtures
19 | Take down, remove existing shower, set aside for potential re-use | No | 8 |  | 0
20 | Take down, remove existing WC, set aside for potential re-use | No | 6 |  | 0
21 | Take down, remove existing lav sink, set aside for potential re-use | No | 6 |  | 0
22 | Take down, remove existing ADA shower, set aside for potential re-use | No | 4 |  | 0
| D2010 - Plumbing Fixtures |  |  |  | 0
D2090 | Other Plumbing Systems
354 | Bain Marie: Cut out 1m wide slot in floor slab and dispose of concrete waste where directed onsite | SY | 4 |  | 0
| D-2090 - Other Plumbing Systems |  |  |  | 0
D3040 | Distribution Systems
24 | Take down, remove existing AC ductwork and accessories (Room 0.08 Pharmacy Store) - assumed 20" x 20" galv insulated duct | SF | 307 |  | 0
| D3040 - Distribution Systems |  |  |  | 0
F2010 | Building Elements Demolition
1 | Carefully take down and remove single leaf door including frame, ironmongery and accessories, set aside for potential re-use | No | 9 |  | 0
2 | Carefully take down and remove double leaf door including frame, ironmongery and accessories, set aside for potential re-use | No | 4 |  | 0
3 | Carefully take down and remove 4'-0" wide internal window including frame and accessories, set aside for potential re-use | No | 3 |  | 0
4 | Take down, remove and dispose partitions where directed on site | LF | 162 |  | 0
5 | Take down, remove and dispose walls where directed on site | LF | 88 |  | 0
6 | Take down, remove and dispose walls to create door opening where directed on site | LF | 7 |  | 0
7 | Removal of tiled upstand in shower, dispose where directed on site | LF | 29 |  | 0
8 | Take down, remove and dispose of railing and pillars offsite | LF | 21 |  | 0
9 | Take down and remove extension above switch room (assume walls), dispose where directed onsite | LF | 20 |  | 0
10 | Stair, walls and pillars to be removed to widen access, dispose where directed on site | SF | 85 |  | 0
11 | Removal of kitchen cupboards 2'-0" wide (assume floor mounted only), dispose offsite | LF | 20 |  | 0
12 | Removal of nurses station 1'-8" wide, dispose offsite | LF | 6 |  | 0
13 | Removal of built in lockers 1'-6" wide, dispose offsite | LF | 15 |  | 0
60 | Take down door Ref. D.9.28A and rehang on frame opposite | No | 1 |  | 0
331 | Take down, remove and dispose where directed onsite veranda balustrades | SF | 215 |  | 0
| F2010 - Building Elements Demolition |  |  |  | 0
| 02 - EXISTING CONDITIONS |  |  |  | 0
31 EARTHWORK
A1010 | Standard Foundations
132 | Kitchen extension; excavate trenches for strip footing | CY | 4 |  | 0
133 | Kitchen extension; level and compact bottom of trenches to receive concrete | SY | 4 |  | 0
134 | Kitchen extension; return fill and ram selected excavated material around foundations | CY | 2 |  | 0
135 | Kitchen extension; dispose of surplus excavated material on site | CY | 2 |  | 0
136 | Kitchen extension; backfill below slab with well compacted Type 1 material | CY | 2 |  | 0
137 | Kitchen extension; DPM - polythene sheet 1000 gauge lapped 12" at joints | SY | 3 |  | 0
253 | Excavate trench and pits for entrance foundation wall and column footings | CY | 4 |  | 0
254 | Level and compact bottom of trench and pits to receive entrance foundation wall and column footing concrete | SY | 4 |  | 0
255 | Return fill and ram selected excavated material around entrance foundation wall and column footings | CY | 2 |  | 0
256 | Spread and level surplus excavated material arising from entrance foundation wall and column footing excavation | CY | 2 |  | 0
372 | Gas bottles Enclosure; excavate trenches for strip footing | CY | 4 |  | 0
373 | Gas bottle Enclosure; level and compact bottom of trenches to receive concrete | SY | 4 |  | 0
374 | Gas Bottle Enclosure; return fill and ram selected excavated material around foundations | CY | 2 |  | 0
375 | Gas Bottle Enclosure; dispose of surplus excavated material on site | CY | 2 |  | 0
376 | Gas Bottle Enclosure; backfill below slab with well compacted Type 1 material | CY | 2 |  | 0
377 | Gas Bottle Enclosure; DPM - polythene sheet 1000 gauge lapped 12" at joints | SY | 3 |  | 0
| A1010 - Standard Foundations |  |  |  | 0
C2010 | Stair Construction
110 | Excavate pits for escape stairs pad footing | CY | 5 |  | 0
111 | Level and compact bottom of pits to receive concrete | SY | 5 |  | 0
112 | Return fill and ram selected excavated material around foundations | CY | 3 |  | 0
113 | Spread and level surplus excavated material on site | CY | 3 |  | 0
162 | Excavate trench for external stair and wall strip footing | CY | 10 |  | 0
163 | Level and compact bottom of trench to receive external stair and wall strip footing concrete | SY | 10 |  | 0
164 | Return fill and ram selected excavated material around external stair foundation | CY | 4 |  | 0
165 | Spread and level surplus excavated material arising from external stair excavation on site | CY | 6 |  | 0
| C2010 - Stair Construction |  |  |  | 0
D2090 | Other Plumbing Systems
353 | Bain Marie: Excavate a trial pit to expose slab edge and dispose excavated material in spoil heap for reuse (assumed 2'x1'x1') | SUM | 1 |  | 0
355 | Bain Marie: Excavate below slab cut out to install drain run and dispose of excavated material in spoil heap for reuse | CY | 2 |  | 0
356 | Bain Marie: Level and compact bottom of excavation | SY | 4 |  | 0
357 | Bain Marie: Backfill with selected material on site | CY | 1 |  | 0
358 | Bain Marie: Polythene sheet | SY | 4 |  | 0
| D2090 - Other Plumbing Systems |  |  |  | 0
| 31 - EARTHWORK |  |  |  | 0
03 | CONCRETE
A1010 | Standard Foundations
126 | Kitchen extension; in-situ concrete to external wall strip footing | CY | 2 |  | 0
127 | Kitchen extension; formwork to external wall strip footing | SY | 4 |  | 0
129 | Kitchen extension; in-situ concrete slab, 6" thick, include for starter bars fixed into the sides of the existing slab | CY | 1 |  | 0
130 | Kitchen extension; Mesh fabric reinforcement to concrete slab, A393 | SY | 8 |  | 0
131 | Kitchen extension; formwork to edges of concrete slab 6" high | SY | 1 |  | 0
257 | Blinding in bottom of entrance foundation wall footing trench and column footing pits, 2" thick plain in-situ concrete (1:4:8) | SY | 4 |  | 0
258 | Reinforced in-situ concrete to entrance foundation wall footing and column footings: 35N/mm2 | CY | 2 |  | 0
259 | Reinforcement to entrance foundation wall strip footing; mesh fabric reinforcement BRC A393 | SY | 5 |  | 0
260 | Reinforcement to entrance column pad footings, 1/2" diameter bars | Lb | 39 |  | 0
261 | Formwork to entrance foundation wall strip footing and column pad footings sides | SY | 5 |  | 0
378 | Gas Bottles Enclosure; in-situ concrete to external wall strip footing | CY | 2 |  | 0
379 | Gas Bottles Enclosure; formwork to external wall strip footing | SY | 4 |  | 0
380 | Gas Bottles Enclosure; in-situ concrete slab, 6" thick, include for starter bars fixed into the sides of the existing slab | CY | 1 |  | 0
381 | Gas Bottles Enclosure; mesh fabric reinforcement to concrete slab, A393 | SY | 4 |  | 0
382 | Gas Bottles Enclosure; formwork to edges of concrete slab 6" high | SY | 1 |  | 0
| A1010 - Standard Foundations |  |  |  | 0
B1010 | Floor Construction
262 | Reinforced in-situ concrete to new entrance columns: 35N/mm2 | CY | 2 |  | 0
263 | Reinforcement to new entrance columns, 5/8" diameter bars | Lb | 272 |  | 0
264 | Reinforcement to new entrance columns, 3/8" diameter stirrups | Lb | 138 |  | 0
265 | Formwork to sides of new entrance columns | SY | 19 |  | 0
266 | Reinforced in-situ concrete to new entrance beams: 35N/mm2 | CY | 3 |  | 0
267 | Reinforcement to new entrance beams, 5/8" diameter bars | Lb | 261 |  | 0
268 | Reinforcement to new entrance beams, 3/8" diameter stirrups | Lb | 254 |  | 0
269 | Formwork to sides of new entrance beams | SY | 35 |  | 0
271 | Reinforced in-situ concrete to new entrance slab: 35N/mm2 | CY | 4 |  | 0
272 | Reinforcement to new entrance slab, 5/8" diameter bars | Lb | 1623 |  | 0
273 | Formwork to sides and soffit of new entrance slab | SY | 25 |  | 0
295 | Allow for connecting existing columns, beams and slabs to new, 5/8" starter bars resin fixed into existing members including drilling and grouting holes and tying into existing reinforcement as indicated on drawings | Lb | 240 |  | 0
307 | Concrete infill to columns | CY | 1 |  | 0
341 | Reinforcement to concrete infill columns; 5/8" diameter bars | Lb | 113 |  | 0
342 | Reinforcement to concrete infill columns; 3/8" diameter stirrups | Lb | 59 |  | 0
| B1010 - Floor Construction |  |  |  | 0
B1020 | Roof Construction
276 | Reinforced in-situ concrete to new pitched concrete beams at entrance: 35N/mm2 | CY | 2 |  | 0
277 | Reinforcement to new pitched concrete beams at entrance, 5/8" diameter bars | Lb | 146 |  | 0
278 | Reinforcement to new entrance pitched concrete beams at entrance, 3/8" diameter stirrups | Lb | 142 |  | 0
279 | Formwork to sides of new pitched concrete beams at entrance | SY | 19 |  | 0
| B1020 - Roof Construction |  |  |  | 0
C2010 | Stair Construction
114 | Blinding in bottom of pits, 2" thick, plain in-situ concrete (1:4:8) | CY | 2 |  | 0
115 | Reinforced in-situ concrete to escape stair pad footings, 35N/mm2 | CY | 2 |  | 0
116 | Reinforcement to escape stair pad footings; 1/2" diameter bars | Lb | 192 |  | 0
117 | Formwork to sides of escape stair pad footing | SY | 9 |  | 0
118 | Reinforced in-situ concrete to escape stair columns, 35N/mm2 | CY | 2 |  | 0
119 | Reinforcement to escape stair columns, 5/8" diameter bars | Lb | 383 |  | 0
120 | Reinforcement to escape stair columns, 3/8" diameter stirrups | Lb | 200 |  | 0
121 | Formwork to sides of escape stair columns | SY | 27 |  | 0
122 | Reinforced in-situ concrete to escape stair and landing, 35N/mm2 | CY | 4 |  | 0
123 | Reinforcement to escape stair and landing, 5/8" diameter bars | Lb | 234 |  | 0
124 | Reinforcement to escape stair and landing, 1/2" diameter bars | Lb | 132 |  | 0
125 | Formwork to sides and soffit of escape stair and landing | SY | 24 |  | 0
166 | Blinding in bottom of external stair and wall trench, 2" thick, plain in-situ concrete (1:4:8) | SY | 10 |  | 0
167 | Reinforced in-situ concrete to external stair and wall strip footing: 35N/mm2 | CY | 4 |  | 0
168 | Reinforcement to external stair and wall strip footing; mesh fabric reinforcement BRC A393 | SY | 19 |  | 0
169 | Formwork to external stair and wall strip footing | SY | 11 |  | 0
171 | Reinforced in-situ concrete to external stair and landing, 35N/mm2 | CY | 4 |  | 0
172 | Reinforcement to external stair and landing, 5/8" diameter bars | Lb | 220 |  | 0
173 | Reinforcement to external stair and landing, 1/2" diameter bars | Lb | 124 |  | 0
174 | Formwork to sides and soffit of external stair and landing | SY | 24 |  | 0
| C2010 - Stair Construction |  |  |  | 0
D2090 | Other Plumbing Systems
359 | Bain Marie: Reinforced in-situ concrete to re-instate cut out | CY | 1 |  | 0
360 | Bain Marie: Reinforcement bars; 1/2" | Lbs | 53 |  | 0
361 | Bain Marie: Dowel bars to slab edges (assumed 1/2" bars, 8" o/c, 1'-4" long) including drilling and grouting holes and tying into existing reinforcement | No | 33 |  | 0
| D2090 - Other Plumbing Systems |  |  |  | 0
G2030 | Pedestrian Paving
107 | Reinforced concrete to new footpath to rear of building with a broom finish, 5" thick | SY | 54 |  | 0
108 | Mesh fabric reinforcement to footpath, BRC A193, include for cutting, bending, placing in position, tying wire and distance blocks also 8" side and end laps | SY | 54 |  | 0
109 | Formwork to edges of footpath, 5" high | SY | 10 |  | 0
149 | Reinforced concrete slab to new concrete path to access new containers, 5" thick | CY | 6 |  | 0
150 | Mesh fabric reinforcement to new concrete path to access new containers; BRC A193, include for cutting, bending, placing in position, tying wire and distance blocks also 8" side and end laps | SY | 39 |  | 0
151 | Formwork to edges of new concrete path to access new containers, 5" high | SY | 6 |  | 0
| G2030 - Pedestrian Paving |  |  |  | 0
| 03 - CONCRETE |  |  |  | 0
04 MASONRY
A1010 | Standard Foundations
128 | Kitchen extension; 6" thick strip footing blockwall built in cement/sand mortar having cores filled solid with concrete and reinforced with 1 No. 1/2" vertical reinforcing bar in each core and 1 No. 1/2" horizontal bar in every third course | SY | 4 |  | 0
293 | Blockwork to entrance wall, 8" thick blockwall built in cement/sand mortar, reinforced with 1 No. 1/2" vertical reinforcing bar in each core and 1 No. 1/2" horizontal bar in every third course | SY | 14 |  | 0
383 | Gas Bottles Enclosure; 6" thick strip footing blockwall built in cement/sand mortar having cores filled solid with concrete and reinforced with 1 No. 1/2" vertical reinforcing bar in each core and 1 No. 1/2" horizontal bar in every third course | SY | 4 |  | 0
| A1010 - Standard Foundations |  |  |  | 0
B2010 | Exterior Walls
16 | New hollow concrete blockwork; 8" thick, built in cement/sand mortar having all cores filled solid with concrete, 1 No. 1/2" diameter vertical reinforcing bar at 8" centres and 1/2" diameter horizontal bar in every third course. | SY | 46 |  | 0
138 | Kitchen extension; new hollow concrete blockwork; 6" thick, built in cement/sand mortar having alternate cores filled solid with concrete and 1/2" diameter reinforcing bars at 16" centres | SY | 18 |  | 0
384 | Gas Bottles Enclosure; new hollow concrete blockwork; 6" thick, built in cement/sand mortar having alternate cores filled solid with concrete and 1/2" diameter reinforcing bars at 16" centres | SY | 18 |  | 0
| B2010 - Exterior Walls |  |  |  | 0
C1010 | Partitions
14 | New hollow concrete blockwork; 4" thick, built in cement/sand mortar having alternate cores filled solid with concrete and 1/2" diameter reinforcing bars at 16" centres | SY | 243 |  | 0
15 | New hollow concrete blockwork; 6" thick, built in cement/sand mortar having alternate cores filled solid with concrete and 1/2" diameter reinforcing bars at 16" centres | SY | 15 |  | 0
| C1010 - Partitions |  |  |  | 0
C2010 | Stair Construction
170 | Blockwork to external stair and wall strip footing, 8" thick hollow blocks reinforced with 1 No. 1/2" vertical reinforcing bar in each core and 1 No. 1/2" horizontal bar in every third course | SY | 52 |  | 0
| C2010 - Stair Construction |  |  |  | 0
| 04 - MASONRY |  |  |  | 0
05 METALS
B1020 | Roof Construction
144 | Kitchen extension; corrugated metal roof sheeting | SY | 6 |  | 0
161 | Metal flashing between existing wall and new roof | YD | 4 |  | 0
330 | Kitchen extension; Mild steel restraint straps to rafters, 30x5 | No | 5 |  | 0
283 | Corrugated metal roof sheeting to entrance roof | SY | 35 |  | 0
296 | Mild steel restraint straps to new entrance roof, 30x5 | No | 18 |  | 0
385 | Gas Bottles Enclosure; corrugated metal roof sheeting | SY | 6 |  | 0
386 | Metal flashing between existing wall and new roof | YD | 4 |  | 0
387 | Gas Bottles Enclosure; Mild steel restraint straps to rafters, 30x5 | No | 5 |  | 0
| B1020 - Roof Construction |  |  |  | 0
| 05 - METALS |  |  |  | 0
06 WOOD, PLASTICS, AND COMPOSITES
All timbers to be pressure treated Southern Yellow Pine or approved equivalent
B1020 | Roof Construction
139 | Kitchen extension; 1"X6" fascia board | LF | 11 |  | 0
140 | Kitchen extension; 2"X4" timber wall plate | LF | 19 |  | 0
141 | Kitchen extension; 2"X6" timber rafters | LF | 24 |  | 0
142 | Kitchen extension; 3/4" marine plywood as roof board | SF | 52 |  | 0
143 | Kitchen extension; 1"X2" battens | LF | 35 |  | 0
145 | Kitchen extension; gutter to match and link to existing | YD | 4 |  | 0
146 | Kitchen extension; rainwater down-pipe to match existing | YD | 4 |  | 0
280 | Timber rafters to entrance roof; 2"X6", strapped down to concrete beams with 30x5 mild steel restraint straps (measured separately) | LF | 157 |  | 0
281 | Plywood as roof boarding to entrance roof; 3/4" thick treated exterior ply | SF | 308 |  | 0
282 | Timber battens to entrance roof; 1"X2" | LF | 206 |  | 0
284 | Rainwater gutter to new entrance roof to match and link to existing | YD | 12 |  | 0
334 | Timber ridge board to entrance roof; 2"X8" | LF | 18 |  | 0
389 | Gas Bottles Enclosure; 1"X6" fascia board | LF | 11 |  | 0
390 | Gas Bottles Enclosure; 2"X4" timber wall plate | LF | 19 |  | 0
391 | Gas Bottles Enclosure; 2"X6" timber rafters | LF | 23 |  | 0
392 | Gas Bottles Enclosure; 3/4" marine plywood as roof board | SF | 50 |  | 0
393 | Gas Bottles Enclosure; 1"X2" battens | LF | 34 |  | 0
394 | Gas Bottles Enclosure; gutter to match and link to existing | YD | 4 |  | 0
395 | Gas Bottles Enclosure; rainwater down-pipe to match existing | YD | 4 |  | 0
| B1020 - Roof Construction |  |  |  | 0
C3020 | Floor Finishes
17 | New floor finish to match existing (tiles) | SY | 52 |  | 0
18 | Make good to existing flooring | SY | 781 |  | 0
| C3020 - Floor Finishes |  |  |  | 0
| 06 - WOOD, PLASTICS, AND COMPOSITES |  |  |  | 0
07 THERMAL AND MOISTURE PROTECTION
C2010 | Stair Construction
305 | Propriety joint sealant to gap between face of existing building and new escape staircase | SF | 3 |  | 0
| C2010 - Stair Construction |  |  |  | 0
| 07 - THERMAL AND MOISTURE PROTECTION |  |  |  | 0
08 OPENINGS
B2020 | Exterior Windows
58 | Supply and install 4'-0"X4'-0" adjustable aluminium louvre window Refer to drawings for details | No | 13 |  | 0
| B2020 - Exterior Windows |  |  |  | 0
B2030 | Exterior Doors
Refer to drawings for details
59 | Supply and install 5'-5" wide X 7'-0 1/2" high double leaf solid core wood entrance door with 2 No. 2'-6" wide X 7-0 1/2" high sidelights, refer to door schedule XXX for details | No | 1 |  | 0
63 | Supply and install 3'-5" wide X 7'-0 1/2" high single leaf solid core aluminium panel external door | No | 2 |  | 0
65 | Supply and install 5'-5" wide X 7'-0 1/2" high double leaf solid core aluminium panel external door | No | 2 |  | 0
388 | Gas Bottles Enclosure; metal cage double gate, 5'-5" wide X 7'-0-1/2" high | No | 1 |  | 0
| B2030 - Exterior Doors |  |  |  | 0
C1020 | Interior Doors
Refer to drawings for details
61 | Supply and install 3'-5" wide X 7'-0 1/2" high single leaf solid core wood panel internal door | No | 23 |  | 0
62 | Supply and install 5'-5" wide X 7'-0 1/2" high double leaf solid core wood panel internal door | No | 1 |  | 0
66 | Supply and install 3'-5" wide X 7'-0 1/2" high single leaf solid core wood panel internal door with 4'-5" wide X 7'-0 1/2" high wood framed sidelight (D.0.02A) | No | 1 |  | 0
67 | Supply and install 3'-5" wide X 7'-0 1/2" high single leaf glass panel wood internal door (lunch and meeting room) | No | 2 |  | 0
369 | Supply and install 3'-5" wide X 7'-0 1/2" high single leaf solid core wood panel internal door with 4'-5" wide X 7'-0 1/2" high wood framed sidelight (D.0.07A, D.9.21) | No | 2 |  | 0
| C1020 - Interior Doors |  |  |  | 0
| 08 - OPENINGS |  |  |  | 0
09 FINISHINGS
C1020 | Interior Doors
51 | Prepare surface and apply two coats oil paint on existing doors and frames | SY | 230 |  | 0
52 | Prepare surface and apply one coat primer and two coats oil paint on new doors and frames | SY | 190 |  | 0
| C1020 - Interior Doors |  |  |  | 0
C2020 | Stair Finishes
339 | Stair balustrade to escape and entrance stairs; 4" thick hollow blockwork | SY | 42 |  | 0
340 | Cement and sand plaster (1:3 mix) to stair balustrade, 3/4" thick on concrete block walls | SY | 81 |  | 0
366 | Bridge balustrade; 4" thick hollow blockwork | SY | 15 |  | 0
367 | Cement and sand plaster (1:3 mix) to bridge balustrade, 3/4" thick on concrete block walls | SY | 31 |  | 0
368 | Prepare surface and apply one coat primer and two coats emulsion paint on bridge balustrade | SY | 31 |  | 0
| C2020 - Stair Finishes |  |  |  | 0
C3010 | Wall Finishes
48 | Make good to painted existing internal walls including preparing surface and applying two coats of emulsion paint | SY | 857 |  | 0
49 | Prepare surface and apply one coat of primer and two coats of emulsion paint on new internal plastered walls | SY | 578 |  | 0
53 | Ceramic tiles to walls | SY | 96 |  | 0
56 | Make good to Sit-on skirting | YD | 732 |  | 0
68 | Cement and sand plaster (1:3 mix) to new internal walls, 1/2" thick on concrete block walls | SY | 560 |  | 0
69 | Cement and sand plaster (1:3 mix) to new external walls, 3/4" thick on concrete block walls | SY | 46 |  | 0
70 | Make good to painted existing external walls including preparing surface and applying two coats of emulsion paint | SY | 563 |  | 0
71 | Prepare surface and apply one coat of primer and two coats of emulsion paint on new external plastered walls | SY | 46 |  | 0
328 | Kitchen extension; Cement and sand plaster (1:3 mix) to external block walls, 3/4" thick | SY | 18 |  | 0
329 | Kitchen extension; Cement and sand plaster (1:3 mix) to internal block walls, 1/2" thick | SY | 18 |  | 0
294 | Cement and sand plaster (1:3 mix) to entrance wall, 3/4" thick on concrete block walls | SY | 27 |  | 0
335 | Prepare surface and apply one coat primer and two coats emulsion paint on entrance wall | SY | 27 |  | 0
336 | Cement and sand plaster (1:3 mix) to entrance stair wall, 3/4" thick on concrete block walls | SY | 22 |  | 0
337 | Prepare surface and apply one coat primer and two coats emulsion paint on entrance stair wall | SY | 22 |  | 0
396 | Cement and sand plaster (1:3 mix) to Gas Bottles Enclosure walls, 3/4" thick on concrete block walls | SY | 36 |  | 0
397 | Prepare surface and apply one coat primer and two coats emulsion paint on Gas Bottles Enclosure walls | SY | 36 |  | 0
| C3010 - Wall Finishes |  |  |  | 0
C3020 | Floor Finishes
332 | Epoxy paint to stairs and bridge | SY | 79 |  | 0
362 | Bain Marie: Make good to floor finish, include for finish | SY | 4 |  | 0
398 | Epoxy paint to Gas Bottles Enclosure floor | SY | 9 |  | 0
| C3020 - Floor Finishes |  |  |  | 0
C3030 | Ceiling Finishes
54 | Make good to painted existing ceiling including preparing surface and applying two coats of emulsion paint | SY | 651 |  | 0
55 | 2'X2' Suspension ceiling system including 2'X2" acoustic ceiling tiles, main tees, cross tees, 12 gauge hanger wire, perimeter wall angle with rawl plug and 40mm drywall stainless steel screws | SY | 190 |  | 0
147 | Kitchen extension; 2"X4" timber joists fixed to walls and running in both directions | LF | 43 |  | 0
148 | Kitchen extension; 1/2" thick moisture resistant gypsum board fixed to ceiling joists, joints taped, filled and finish smooth | SF | 32 |  | 0
333 | Prepare surface and apply one coat primer and two coats oil paint on exposed rafters at new entrance | SY | 35 |  | 0
399 | Gas Bottles Enclosure; prepare surface and apply one coat primer and two coats oil paint on exposed rafters | SY | 6 |  | 0
400 | Kitchen extension: prepare surface and apply one coat primer and two coats emulsion paint on gypsum ceiling | SY | 4 |  | 0
| C3030 - Ceiling Finishes |  |  |  | 0
| 09 - FINISHINGS |  |  |  | 0
10 SPECIALTIES
B2030 | Exterior Doors
102 | Heavy duty exterior door handles by Union or approved equivalent | No | 7 |  | 0
106 | Heavy duty stainless steel hinges to external doors | No | 21 |  | 0
365 | Electronic lock sets | No | 7 |  | 0
370 | Emergency release | No | 4 |  | 0
| B2030 - Exterior Doors |  |  |  | 0
C1020 | Interior Doors
101 | Cylinder lock set with stainless steel satin brush finished lever handles for internal doors by Union or approved equivalent | No | 29 |  | 0
103 | Heavy duty stainless steel hinges to internal doors | No | 87 |  | 0
105 | Emergency release | No | 7 |  | 0
363 | Kick-plates | No | 11 |  | 0
364 | Electronic lock sets | No | 4 |  | 0
| C1020 - Interior Doors |  |  |  | 0
C1030 | Fittings
All restroom accessories to be of a hospital grade, Ideal or American Standard
74 | Restroom accessories - New Hat & Coat Hook | No | 3 |  | 0
75 | Restroom accessories - New wall mounted mirror, 2'-0" X 1'-0" | No | 3 |  | 0
76 | Restroom accessories - New shelf in ground floor WC, 2'-0" X 0'-6" | No | 1 |  | 0
77 | Restroom accessories - New wall mounted paper towel dispenser, hospital grade | No | 3 |  | 0
78 | Restroom accessories - New wall mounted soap dispenser, hospital grade | No | 3 |  | 0
79 | Restroom accessories - New toilet roll holder, hospital grade | No | 3 |  | 0
| C1030 - Fittings |  |  |  | 0
| 10 - SPECIALTIES |  |  |  | 0
12 FURNISHINGS
E2010 | Fixed Furnishings
All timbers to be pressure treated Southern Yellow Pine or approved equivalent. Refer to Equipment Plans, drawings 1500 & 1590.
72 | New bench in ground floor reception area, approximately 6'-5" long X 1'-10" wide | No | 7 |  | 0
73 | New reception counter in ground floor Medical Records Room, approximately 4'-5" long X 1'-6" wide, include for countertop | No | 1 |  | 0
80 | New reception worktop with legs in GF Pharmacy, solid, non-porous, include for countertop | No | 1 |  | 0
81 | New worktop in GF pharmacy to accommodate a double sink with drainer, L-shaped , approximately 18'-5" long X 2'-6" wide, solid, non-porous, include for countertop | No | 1 |  | 0
82 | New base cupboard for storage; 2 doors | No | 26 |  | 0
83 | New freestanding shelves, 6'-0" wide X 1'-6" deep | No | 22 |  | 0
84 | New Coat hooks in GF Coats area | No | 12 |  | 0
85 | New worktop in GF Phlebotomy, approximately 7'-0" long X 2'-0" deep, solid, non-porous | No | 1 |  | 0
86 | New wall mounted cupboard for storage; 2 doors | No | 7 |  | 0
87 | New Microbiology worktop to accommodate a single sink with drainer, approximately 12'-4" long X 2'-0" wide, solid, non-porous, include for counter top | No | 1 |  | 0
88 | New worktop with legs in GF Pharmacy, solid, non-porous, refer to drawing 1100 for details | No | 3 |  | 0
89 | New GF Pathology lab worktop with legs, approximately 21'-0" long X 2'-0" wide, solid, non-porous, include for countertop | No | 1 |  | 0
90 | New GF Pathology lab C-shaped worktop approximately 20'-0" long X 2'-5" wide, solid, non-porous, include for counter top | No | 1 |  | 0
91 | New GF Pathology lab L-shaped worktop, solid, non-porous, include for counter top | No | 1 |  | 0
92 | New GF Wash-up worktop to accommodate a single sink with drainer, approximmately 12'-4" long X 2'-4" wide, solid, non-porous, include for counter top | No | 1 |  | 0
93 | New shelf in Cleaner's Cupboard, 20" wide X 12" deep | No | 1 |  | 0
94 | New GF Biomedical area worktop, approximately 4'-0" long X 1'-5" wide, solid, non-porous, include for countertop | No | 1 |  | 0
95 | New freestanding shelves, 4'-0" wide X 1'-6" deep | No | 2 |  | 0
96 | New Drying & Ironing Room worktop, approximately 12'-2" long X 2'-0" deep, solid, non-porous and temperature resistant | No | 1 |  | 0
97 | New freestanding shelves, 5'-0" wide X 1'-6" deep | No | 1 |  | 0
98 | New freestanding shelves, 6'-0" wide X 1'-0" deep | No | 2 |  | 0
99 | New freestanding shelves, 7'-0" wide X 2'-0" deep | No | 3 |  | 0
327 | New LGF lunch room worktop to accomodate a single sink with drainer, approximately 8'-0" long X 2" deep | No | 1 |  | 0
338 | Handrail to stairs | YD | 29 |  | 0
| E2010 - Fixed Furnishings |  |  |  | 0
E2020 | Movable Furnishings
100 | Allow for transferring and/ decomissioning and recommisioning items such as desks, chairs, computers, telephones, filing cabinets, bins, tables, fridges, cupboards,, shelves, Analyser, hot water dispenser, small oven, trolleys, serving racks, sack holder, dryer machines, washing machines, cookers, freezers, ironing board etc from the old hospital to Margetson House in the locations indicated on the drawings. | SUM
| E2020 - Movable Furnishings |  |  |  | 0
| 12 - FURNISHINGS |  |  |  | 0
22 PLUMBING
D2010 | Plumbing Fixtures
All plumbing fixtures to be of a hospital grade, Ideal or American Standard
33 | (SS2) Stainless steel double sink with drainer including faucets, drainage assembly and fixings | No | 1 |  | 0
40 | (SS3) Cleaners sink including faucets, drainage assembly and fixings | No | 1 |  | 0
34 | (SS4) Laundry sink including faucets, drainage assembly and fixings | No | 1 |  | 0
35 | (WC1) Toilet including cistern, flush valve and fixings | No | 3 |  | 0
36 | (WB1) Clinical hand wash sink including faucets, drainage assembly and fixings | No | 1 |  | 0
41 | (WHB1) Wash hand basin including faucets, drainbage assembly and fixings | No | 3 |  | 0
45 | Stainless steel sink - Potwash - (7'-3" W x 2'-2" D x 5'-7" H) | No | 1 |  | 0
44 | Stainless steel sink - Potwash - (4'-9" W x 2'-2" D x 3'-5" H) | No | 1 |  | 0
38 | Hot water dispenser | No | 1 |  | 0
371 | (SS1) Stainless steel single sink with drainer including faucets, drainage assembly and fixings | No | 3 |  | 0
| D2010 - Plumbing Fixtures |  |  |  | 0
D2020 | Domestic Water Distribution
30 | Plumbing fixture shut off valves | No | 27 |  | 0
42 | Plumbing connections to items of equipment | No | 3 |  | 0
306 | Disconnect & remove existing domestic HW Generator and replace with like for like including accessories, supports and fixings (assumed size and type 135,000 BTU, Electric) | No | 1 |  | 0
308 | Existing domestic HW Generator to be retained, condition to be confirmed by client (assumed size and type 135,000 BTU, Electric) | No | 1 |  | 0
309 | Disconnect & remove existing domestic HW Pump and replace with like for like including accessories, supports and fixings | No | 2 |  | 0
310 | Provide 35mm copper pipe connection to MCWS entering building from isolation valve including accessories | No | 1 |  | 0
311 | (CWS) 42mm insulated copper pipe including hangers, valves, accessories and fixings | LF | 16 |  | 0
313 | (CWS) 35mm insulated copper pipe including hangers, valves, accessories and fixings | LF | 64 |  | 0
314 | (CWS) 28mm insulated copper pipe including hangers, valves, accessories and fixings | LF | 24 |  | 0
315 | (CWS) 22mm insulated copper pipe including hangers, valves, accessories and fixings | LF | 262 |  | 0
316 | (CWS) 15mm insulated copper pipe including hangers, valves, accessories and fixings | LF | 221 |  | 0
317 | (HWS/R) 35mm insulated copper pipe including hangers, valves, accessories and fixings | LF | 40 |  | 0
318 | (HWS/R) 28mm insulated copper pipe including hangers, valves, accessories and fixings | LF | 67 |  | 0
319 | (HWS/R) 22mm insulated copper pipe including hangers, valves, accessories and fixings | LF | 233 |  | 0
320 | (HWS/R) 15mm insulated copper pipe including hangers, valves, accessories and fixings | LF | 497 |  | 0
| D2020 - Domestic Water Distribution |  |  |  | 0
D2030 | Sanitary Waste
297 | 40mm (SAN/Vent) drainage pipe including valves, accessories and fixings | LF | 11 |  | 0
299 | 50mm (SAN/Vent) drainage pipe including valves, accessories and fixings | LF | 301 |  | 0
300 | 75mm (SAN/Vent) drainage pipe including valves, accessories and fixings | LF | 45 |  | 0
301 | 110mm (SAN/Vent) drainage pipe including valves, accessories and fixings | LF | 69 |  | 0
302 | 50mm (SAN/Vent) pipe connection to buried drainage pipe including accessories | No | 12 |  | 0
303 | 75mm (SAN/Vent) pipe connection to buried drainage pipe including accessories | No | 2 |  | 0
304 | 110mm (SAN/Vent) pipe connection to buried drainage pipe including accessories | No | 3 |  | 0
| D2030 - Sanitary Waste |  |  |  | 0
D2040 | Rain Water Drainage
64 | 6" gutter to kitchen extension including connection to existing | LF | 28 |  | 0
| D2040 - Rain Water Drainage |  |  |  | 0
D2090 | Other Plumbing Systems
29 | Type L soft copper (gas) pipework including valves, manifolds, accessories, insulation and fixings | LF | 84 |  | 0
47 | Testing & Commissioning of all electrical systems as specified. | No | 6 |  | 0
321 | Allow for dosing and flushing pipework in accordance with specified details | Item | 1 |  | 0
322 | Testing & commission Plumbing Installation including flushing pipework systems | Item | 1 |  | 0
| D2090 - Other Plumbing Systems |  |  |  | 0
| 22 - PLUMBING |  |  |  | 0
23 HEATING, VENTILATING, AND AIR CONDITIONING
D3030 | Cooling Generating Systems
351 | Remove and dispose damaged existing wall mounted indoor units | No | 27 |  | 0
350 | Remove existing (12000 BTU/h) wall mounted Evap units, carry out repairs & reinstall | No | 2 |  | 0
349 | Remove existing (18000 BTU/h) wall mounted Evap units, carry out repairs & reinstall | No | 3 |  | 0
348 | Remove existing (24000 BTU/h) wall mounted Evap units, carry out repairs & reinstall | No | 2 |  | 0
347 | Remove existing (30000 BTU/h) wall mounted Evap units, carry out repairs & reinstall | No | 1 |  | 0
346 | Supply & install new wall mounted AC Evap units 12,000 BTU/h | No | 20 |  | 0
345 | Supply & install new wall mounted AC Evap Evap units 18,000 BTU/h | No | 5 |  | 0
344 | Supply & install new wall mounted AC Evap units 24,000 BTU/h | No | 1 |  | 0
343 | Supply & install new wall mounted AC Evap units 30,000 BTU/h | No | 1 |  | 0
222 | Supply & install (ext) wall mounted VRV type condenser (COND-01) 19.1kW cooling, 400v 3ph including accessories, supports and fixings | No | 1 |  | 0
223 | Supply & install (ext) wall mounted VRV type condenser (COND-02) 10.3kW cooling, 230v 1ph including accessories, supports and fixings | No | 1 |  | 0
224 | (Supply & install (ext) wall mounted VRV type condenser (COND-03) 10.8kW cooling, 230v 1ph including accessories, supports and fixings | No | 1 |  | 0
225 | Supply & install (ext) wall mounted VRV type condenser (COND-04) 19.6kW cooling, 400v 3ph including accessories, supports and fixings | No | 1 |  | 0
226 | Supply & install (ext) wall mounted Twin Split type condenser (COND-05) 35.5kW cooling, 3ph including accessories, supports and fixings | No | 1 |  | 0
227 | Supply & install (ext) wall mounted VRV type condenser (COND-06) 31.0kW cooling, 400v 3ph including accessories, supports and fixings | No | 1 |  | 0
228 | Supply & install (ext) wall mounted Split type condenser (COND-07) 3.1kW cooling, 1ph including accessories, supports and fixings | No | 1 |  | 0
| D3030 - Cooling Generating Systems |  |  |  | 0
D3040 | Distribution Systems
229 | (EF-01), ceiling void duct mounted extract fan (44 l/s), standalone manual controls, 1ph, 0.19A including accessories, supports and fixings | No | 1 |  | 0
230 | (EF-02), ceiling void duct mounted extract fan (99 l/s), standalone manual controls, 1ph, 0.26A including accessories, supports and fixings | No | 1 |  | 0
231 | (EF-03), ceiling void duct mounted extract fan (22 l/s), standalone manual controls, 1ph, 0.19A including accessories, supports and fixings | No | 1 |  | 0
232 | (EF-04), through wall mounted extract fan (15 l/s), light switch with 15mins overrun controls, 1ph, 0.19A including accessories, supports and fixings | No | 1 |  | 0
233 | (EF-05, ceiling void duct mounted extract fan (88 l/s), standalone manual controls, 1ph, 0.26A including accessories, supports and fixings | No | 1 |  | 0
234 | (EF-06), ceiling void duct mounted extract fan (114 l/s), standalone manual controls, 1ph, 0.26A including accessories, supports and fixings | No | 1 |  | 0
235 | (EF-07), kitchen extract fan external mount (1051 l/s), manual with gas safety interlock controls, 3ph, 1.1A including accessories, supports and fixings | No | 1 |  | 0
236 | (SF-01), ceiling void duct mounted extract fan (44 l/s), standalone manual controls, 1ph, 0.19A including accessories, supports and fixings | No | 1 |  | 0
237 | (SF-02), ceiling void duct mounted extract fan (22 l/s), standalone manual controls, 1ph, 0.19A including accessories, supports and fixings | No | 1 |  | 0
238 | (SF-03), ceiling void duct mounted extract fan (88 l/s), standalone manual controls, 1ph, 0.19A including accessories, supports and fixings | No | 1 |  | 0
239 | (EG-01, 02, 05) 125 dia. egg crate extract grille (0.02 cm/s) including plenum box, VCD, accessories & fixings | No | 3 |  | 0
240 | (EG-03, 04, 08, 09) 200 dia. egg crate extract grille (0.045 cm/s) including plenum box, VCD, accessories & fixings | No | 4 |  | 0
241 | (EG-06, 07) 160 dia. egg crate extract grille (0.04 cm/s) including plenum box, VCD, accessories & fixings | No | 2 |  | 0
242 | (SD-04, 05) 160 dia. egg crate extract grille (0.04 cm/s) including plenum box, VCD, accessories & fixings | No | 3 |  | 0
243 | (SD-04, 05) 160 dia. egg crate extract grille (0.04 cm/s) including plenum box, VCD, accessories & fixings | No | 1 |  | 0
244 | (LV-01) 250 x 250 ext supply air louvre, (44 l/s) serving SF-01 including accessories & fixings | No | 1 |  | 0
245 | (LV-02) 250 x 250 ext extract air louvre, (44 l/s) serving EF-01 including accessories & fixings | No | 1 |  | 0
246 | (LV-03) 250 x 250 ext supply air louvre, (22 l/s) serving SF-02 including accessories & fixings | No | 1 |  | 0
247 | (LV-04) 350 x 350 ext extract air louvre, (99 l/s) serving EF-02 including accessories & fixings | No | 1 |  | 0
248 | (LV-05) 250 x 250 ext extract air louvre, (22 l/s) serving EF-03 including accessories & fixings | No | 1 |  | 0
249 | (LV-06) 350 x 350 ext extract air louvre, (88 l/s) serving EF-05 including accessories & fixings | No | 1 |  | 0
250 | (LV-07) 350 x 350 ext supply air louvre, (88 l/s) serving SF-03 including accessories & fixings | No | 1 |  | 0
251 | (LV-08) 500 x 300 ext extract air louvre, (114 l/s) serving EF-06 including accessories & fixings | No | 1 |  | 0
270 | 225 x 200 cable tray - (supports for refrigerant pipework) including accessories, brackets and fixings | LF | 663 |  | 0
275 | Insulated refrigerant piping (suction/liquid lines) fixed to cable tray including accessories and fixings | LF | 2409 |  | 0
285 | 26 gauge galv circular (supply) ductwork including accessories, supports and fixings | SF | 152 |  | 0
286 | 26 gauge galv circular (extract) ductwork including accessories, supports and fixings | SF | 255 |  | 0
287 | 26 gauge galv circular (kitchen extract) ductwork including accessories, supports and fixings | SF | 278 |  | 0
288 | Kitchen extract canopy (2450 x 1200 x 400) including grease filtration, accessories, supports and fixings | No | 1 |  | 0
289 | 6" flexible round duct including brackets, straps, accessories and fixings | LF | 65 |  | 0
290 | 8" flexible round duct including brackets, straps, accessories and fixings | LF | 28 |  | 0
| D3040 - Distribution Systems |  |  |  | 0
D3060 | Controls & Instrumentations
323 | Thermostats and manual remote control | No | 35 |  | 0
| D3060 - Controls & Instrumentations |  |  |  | 0
D3070 | Systems Testing & Balancing
324 | Test & Commission (Mech AC installation) in accordance with the specification | Item | 1 |  | 0
| D3070 - Systems Testing & Balancing |  |  |  | 0
| 23 - HEATING, VENTILATING, AND AIR CONDITIONING |  |  |  | 0
26 ELECTRICAL
D5010 | Electrical Service & Distribution
196 | Main Site Panel 24way 100A TP&N Panel located (Switchroom 9.34) including 100A TP&N isolator, RCBO's (13@10A SP, 4@20A SP, 17@32A SP, 1@45A SP, 4@20A TP, 1@32A TP), accessories and fixings | No | 1 |  | 0
| D5010 - Electrical Service & Distribution |  |  |  | 0
D5020 | Lighting and Branch Wiring
43 | Electrical connections to items of equipment | No | 38 |  | 0
175 | (Ref. A); 600 x 600 recessed LED panel light fixture as Dextra - Mode Edge - MODE L40 - 36.3w including lamps, accessories, supports and fixings | No | 9 |  | 0
176 | (Ref. A1); 600 x 600 recessed LED panel light fixture as Dextra - Mode Edge - MODE L30 - 25.6w including lamps, accessories, supports and fixings | No | 18 |  | 0
177 | (Ref. B); 600 x 600 surface LED panel light fixture as Dextra - Mode Edge - MODS L35 - 26.5w including lamps, accessories, supports and fixings | No | 23 |  | 0
178 | (Ref. C); Linear recessed LED light fixture IP65 as Dextra - HYDRA HYDL26PC45 - 1200mm x 150mm 23w "SUS" suspended including lamps, accessories, supports and fixings | No | 38 |  | 0
179 | (Ref. D); Slim-line LED downlight fixture as Dextra - LEDEX LDX DL L20X4 19.8w including lamps, accessories, supports and fixings | No | 45 |  | 0
180 | (Ref. F) External circular LED light fixture as Dextra - Amenity Plus AMC L20 BO 14.4w with integral presence & daylight sensor R25E including lamps, accessories, supports and fixings | No | 16 |  | 0
201 | (Ref. F/E) External circular LED emergency light fixture as Dextra - Amenity Plus AMC L20 BO 14.4w with integral presence & daylight sensor R25E including lamps, battery, accessories, supports and fixings | No | 31 |  | 0
181 | (Ref. G); Linear suspended LED light fixture IP65 as Dextra - Elemenet ELL 15L37 - 1200mm x 215mm 24.7w including lamps, accessories, supports and fixings | No | 2 |  | 0
182 | (Ref. E1); Open area recessed LED emergency light fixture as Thorlux - Firefly open area with Smart Scan including lamps, accessories, supports and fixings | No | 10 |  | 0
183 | (Ref. E2); Open area recessed LED emergency light fixture as Thorlux - Firefly corridor with Smart Scan including lamps, accessories, supports and fixings | No | 25 |  | 0
184 | (Ref. EXIT); Surface mounted LED directional exit light fixture as Philip Payne Arcaplus with Smart Scan including lamps, accessories, supports and fixings | No | 11 |  | 0
185 | Motion Sensor (presence & daylight), PIR 10mins duration including accessories and fixings | No | 5 |  | 0
187 | 1 way switch including faceplate, backbox, accessories and fixings | No | 28 |  | 0
188 | 2 way switch including faceplate, backbox, accessories and fixings | No | 16 |  | 0
202 | 1.5mm 2c MICC/LSF sheath cable including accessories, clips and fixings (lighting) | LF | 3324 |  | 0
190 | 13A single switch socket outlet including faceplate, backbox, accessories and fixings | No | 7 |  | 0
191 | 13A twin switch socket outlet including faceplate, backbox, accessories and fixings | No | 54 |  | 0
192 | 110v duplex receptacle including faceplate, backbox, accessories and fixings | No | 58 |  | 0
193 | Unswitched fused connection unit including faceplate, backbox, accessories and fixings | No | 45 |  | 0
194 | Data outlet including faceplate, backbox, accessories and fixings | No | 33 |  | 0
199 | 25A TPN isolator including accessories and fixings (mech ac items) | No | 1 |  | 0
195 | 20A TPN isolator including accessories and fixings (mech ac items) | No | 3 |  | 0
200 | 10A TPN isolator including accessories and fixings (mech ac items) | No | 2 |  | 0
252 | Step down transformer (TX) including accessories and fixings | No | 2 |  | 0
197 | Dado trunking including accessories and fixings | LF | 164 |  | 0
204 | 2.5mm 2c MICC/LSF sheath cable including accessories, clips and fixings (small power) | LF | 1050 |  | 0
205 | 4mm 2c MICC/LSF sheath cable including accessories, clips and fixings (small power) | LF | 5246 |  | 0
206 | 6mm 3c XLPE/SWA/LSF cable including accessories, cleats and fixings (mech ac items) | LF | 98 |  | 0
207 | 10mm 3c XLPE/SWA/LSF cable including accessories, cleats and fixings (mech ac items) | LF | 252 |  | 0
| D5020 - Lighting and Branch Wiring |  |  |  | 0
D5090 | Other Electrical Systems
325 | Testing & Commissioning of all electrical systems as specified. | Item
| D5090 - Other Electrical Systems |  |  |  | 0
| 26 - ELECTRICAL |  |  |  | 0
27 COMMUNICATIONS
D5030 | Communications & Security
352 | New computer server (3'-4" W x 5'-8" H x 2'-8" D) including equipment, conduit, cabling accessories | No | 1 |  | 0
| D5030 - Communications & Security |  |  |  | 0
| 27 - COMMUNICATIONS |  |  |  | 0
28 ELECTRONIC SAFETY AND SECURITY
D5090 | Other Electrical Systems
208 | Smoke detector including accessories and fixings (FA) | No | 23 |  | 0
209 | Smoke detector with sounder including accessories and fixings (FA) | No | 15 |  | 0
210 | Heat detector with sounder including accessories and fixings (FA) | No | 3 |  | 0
211 | Manual call point including accessories and fixings (FA) | No | 9 |  | 0
212 | (FAP) Fire alarm ontrol panel including accessories, supports and fixings (FA) | No | 1 |  | 0
214 | 1.5mm 2c MICC/LSF sheath cable including accessories, clips and fixings (FA) | LF | 2040 |  | 0
326 | Testing & Commissioning of Fire Alarm installation as specified. | Item | 1 |  | 0
| D5090 - Other Electrical Systems |  |  |  | 0
| 28 - ELECTRONIC SAFETY AND SECURITY |  |  |  | 0

## MHS
NEW NATIONAL HOSPITAL ST. JOHN, MONSTERRAT
MARGETSON HOUSE REFURBISHMENT
SUMMARY

## Summary
NEW NATIONAL HOSPITAL
MARGETSON HOUSE REFURBISHMENT
SUMMARY PAGE
Ref | Description | Total Cost EC$
| Preliminaries and General Conditions | 0
02 | Existing Conditions
D2010 | Plumbing Fixtures | 0
D2090 | Other Plumbing Systems | 0
D3040 | Distribution Systems | 0
F2010 | Building Elements Demolition | 0
| 02 - Existing Conditions | 0
31 | Earthwork
A1010 | Standard Foundations | 0
C2010 | Stair Construction | 0
D2090 | Other Plumbing Systems | 0
| 31 - Earthwork | 0
03 | Concrete
A1010 | Standard Foundations | 0
B1010 | Floor Construction | 0
B1020 | Roof Construction | 0
C2010 | Stair Construction | 0
D2090 | Other Plumbing Systems | 0
G2030 | Pedestrian Paving | 0
| 03 - Concrete | 0
04 | Masonry
A1010 | Standard Foundations | 0
B2010 | Exterior Walls | 0
C1010 | Partitions | 0
C2010 | Stair Construction | 0
| 04 - Masonry | 0
05 | Metals
B1020 | Roof Construction | 0
| 05 - Metals | 0
06 | Wood, Plastics, and Composites
B1020 | Roof Construction | 0
C3020 | Floor Finishes | 0
| 06 - Wood, Plastics, and Composites | 0
07 | Thermal and Moisture Protection
C2010 | Stair Construction | 0
| 07 - Thermal and Moisture Protection | 0
08 | Openings
B2020 | Exterior Windows | 0
B2030 | Exterior Doors | 0
C1020 | Interior Doors | 0
| 08 - Openings | 0
09 | Finishings
C1020 | Interior Doors | 0
C2020 | Stair Finishes | 0
C3010 | Wall Finishes | 0
C3020 | Floor Finishes | 0
C3030 | Ceiling Finishes | 0
| 09 - Finishings | 0
10 | Specialties
B2030 | Exterior Doors | 0
C1020 | Interior Doors | 0
C1030 | Fittings | 0
| 10 - Specialties | 0
12 | Furnishings
E2010 | Fixed Furnishings | 0
E2020 | Movable Furnishings | 0
| 12 - Furnishings | 0
22 | Plumbing
D2010 | Plumbing Fixtures | 0
D2020 | Domestic Water Distribution | 0
D2030 | Sanitary Waste | 0
D2040 | Rain Water Drainage | 0
D2090 | Other Plumbing Systems | 0
| 22 - Plumbing | 0
23 | Heating, Ventilating, and Air Conditioning
D3030 | Cooling Generating Systems | 0
D3040 | Distribution Systems | 0
D3060 | Controls & Instrumentations | 0
| 23 - Heating, Ventilating, and Air Conditioning | 0
26 | Electrical
D5010 | Electrical Service & Distribution | 0
D5020 | Lighting and Branch Wiring | 0
| 26 - Electrical | 0
27 | Communications
D5030 | Communications & Security | 0
| 27 - Communications | 0
28 | Electronic Safety and Security
D5090 | Other Electrical Systems | 0
| 28 - Electronic Safety and Security | 0
TOTAL CONSTRUCTION COST |  | 0